## Introduction
ClimateFIRST created by Jeremy Kohlitz, Ian Cunningham, Jay Falletta and Juliet Willetts - University of Technology Sydney, Institute for Sustainable Futures
ClimateFIRST Climate framework to improve the resilience of sanitation technologies
5. Overall resilience
Consider the overall resilience of the sanitation technology
Summary reports
The last four tabs summarise: (i) the resilience scores, (ii) impacts of hazards, (iii) design strengths, and (iv) design improvements
1. Scoping
Define what parts of the sanitation technology are to be included in the assessment.
2. Hazardous events & trends
Indicate which climate related hazardous events or trends are relevant to your assessment.
4. Design features
Assess the extent to which the sanitation technology incorporates resilient design features
What is this assessment? ClimateFIRST is a process to consider how climate-related hazards can affect a sanitation technology and how the risks of these hazards can be reduced through technology design. It is intended for onsite and decentralised containment and treatment sanitation technologies.
Why do this assessment? This assessment aids in identifying climate-related hazards that should be accounted for in sanitation technology design, highlighting strengths in the current sanitation technology design, inspiring ideas for design improvements, and facilitating group discussion on the overall climate resilience of a sanitation technology.
Who is this framework for? The framework is relevant for sanitation technology designers, research and development personnel, commercial partners and implementation teams in low- and middle-income countries.
3. Hazards
Assess the level of impact that specific hazards are likely to have on the sanitation technology

## 1. Scoping
1 | Scoping | Step 1: Define what parts of the sanitation technology are being included in the assessment.
Instructions: Fill in the grey boxes in the table below. Hover over the cells or refer to the accompanying guidelines for more details.
| Sanitation Technology Description |  | Assessment Team
| Detail | Response | Name | Details
| A. Technology name | Anaerobic Baffled Reactor (ABR) | Freya Mills | UTS-ISF
| B. Assessment date | 2023-09-28 | Jeremy Kohlitz | UTS-ISF
| C. Technology description | 6 baffled reactors and 3 anaerobic filters, concrete structure with reinforcement. Servicing 30-50 people. | Ian Cunningham | UTS-ISF
|  |  | Nuhu Amin | UTS-ISF
| D. Assessed location or context | Banjarmasin, Indonesia | Juliet Willetts | UTS-ISF
| E. Included components | ABR chambers; pipes going from dwelling compound to inlet chamber; outlet pipe; manholes; blackwater inputs
| F. Excluded components | Latrine superstructure; toilet/pan; non-blackwater inputs; pipework within house/building; technology design does not include a soak pit.
Note on D6: Brief description of the technology and identification of what is in and out of the asssessment scope.
Note on D8: The name of the sanitation technology. Example: Septic Tank
Note on D9: The date(s) the assessment was conducted.
Note on D10: Briefly describe the sanitation technology. Example (Septic Tank): Underground two-chamber concrete septic tank with soak pit. Soak pit is built with pre-cast reinforced unlined concrete rings with no based. Soak pit is not filled with gravel.
Note on D12: What location is the sanitation technology assessed for? (e.g. country, region, state) Example: Rural, coastal Bangladesh.
Note on D13: What components of the sanitation technology are included in this assessment? Example: Septic tank; soak pit; pipe from tank to the soak pit; ventilation pipe
Note on D15: What components of the sanitation technology are excluded from this assessment? Example: Superstructure; pipes from toilet to the tank
Note on G6: The individuals working on this assessment.

## 2. Hazardous events and trends
2 | Hazardous events & trends | Step 2: Indicate what climate related hazardous events or trends are relevant to your assessment.
Instructions: Select hazardous events and trends that are relevant for the climate context in which you are assessing the sanitation technology and fill in the grey boxes in the table below. Hover over the cells or refer to the accompanying guidelines for more details.
Hazardous events & trends (HET) |  | Is the HET relevant? | HET Characteristics
💦 | Flood Fluvial flooding (overflowing of a river or other water body) and pluvial flooding (precipitation intensity exceeds drainage capacity) | ✅ Yes | Multiple flooding events per year due to fluvial flooding
🌧 | Changing precipitation patterns Increased variability in seasonal precipitation patterns and inter-annual precipitation | ✅ Yes | Wet season and dry season with increasing variability due to climate change
🌊 | High sea level Permanent inundation from sea level rise or temporary seawater intrusion/coastal flooding due to sea level rise, storm surge, high tide or wave setup | ✅ Yes | Not coastal, but rivers are hydrologically connected to the tide, so groundwater and river levels go up with sea level rise. Rivers are brackish.
🔥 | Fire weather Weather conditions (temperature, soil moisture, humidity, and wind) that trigger and sustain fires | ✅ Yes | Fire risk is mostly driven by human activities, particularly in informal settlements
💨 | Severe wind High wind velocity due to thunderstorms, wind gusts, tornados, or cyclones | ✅ Yes | Strong storms are a risk, but cyclones are not a high risk
🌵 | Droughts Episodic combination of low rainfall and runoff deficit, and evaporation that leads to dry soil (i.e. hydrological drought) | ✅ Yes | Droughts are relatively lower risk compared to floods, but water shortages can occur
🌡 | Changing air temperature Increased variability in diurnal and seasonal air temperature | ✅ Yes | Not a lot of temperature variability as temperature stay around 20 - 30 degrees annually
☀️ | Extreme heat Episodic high surface air temperature events that are potentially exacerbated by humidity | ✅ Yes | Exposed to extreme heat waves and high humidity annually
Note on E6: Indicate if the HET is relevant to the context in which you are assessing the ST. For example, if the ST is being assessed in a context that is not coastal and air temperature does not vary significantly, the 'high sea level' and 'changing air temperature' HETs may be deselected.
Note on F6: Provide comments on the nature of the hazardous event or trend in the context in which you are assessing and how climate change is likely to influence it. For example, flooding events are common in the wet season. These are expected to increase in intensity and frequency due to climate change

## 3. Hazards
3 | Hazards | Step 3: Assess the level of impact that specific hazards are likely to have on the sanitation technology. |  |  | Selected 'Hazardous event and trend' (HETs)
💦 Floods
🌧 Changing precipitation patterns
🌊 High sea level
🔥 Fire weather
💨 Severe wind
🌵 Drought
🌡 Changing air temperature
☀️ Extreme heat
Instructions - For each hazard (An example is provided at the bottom of the page. Hover over the cells or refer to the accompanying guidelines for more details): 1) Hover over the potential hazard to read a specific example of the hazard. 2) Consider whether the hazard is relevant for your sanitation technology. If a hazard is irrelevant (e.g. 'increased levels of receiving waterways' is irrelevant if the sanitation technology does not discharge to a waterway), select No. 3) If the hazard is relevant, select Yes and give an impact rating based on how severely the sanitation technology would be disrupted if it was exposed to that specific example of the hazard. If the hazard is irrelevant, don't give it a rating. 4) Provide a brief justification for your rating.
| Potential Hazard | All hazards for relevant HETs | Relevant? | Impact Rating | Justification
0 | Landslides | 💦 | ⛔️ No |  |  | 0
1 | Corrosion | 🌊🌵 | ✅ Yes | Moderate Impact | The ABR is deployed in an area of high groundwater and is/will be subject, flooding, high rainfall and coastal inundation. The concrete construction (armouring and strengthening) likely provides some mitigation to buoyancy forces. However, because it is buried and the nature of the hazard/CIDs there is still potential for moderate impact. | 1
1 | Erosion | 💦🌊 | ✅ Yes | Moderate Impact | Salt water from coastal flooding could corrode the rebar in the ABR, weakening it over time. Corrosion will be difficult to observe as rebar is not exposed. | 1
1 | Expansion / contraction of soils | 🌧🌊🌵🌡 | ✅ Yes | Low Impact | The nature of this hazard depends on the reactivity of the soils. If the ABR is installed to specifications (with appropriate concrete mixes, i.e armoring and strengthening), this is unlikely to be an issue. | 0
1 | Exposure to flames | 🔥 | ✅ Yes | Low Impact | The concrete construction (armoring and strengthening) means impact of flames would be minimal on the main ABR structure. Most of the pipes going to the ABR are buried. Those that are exposed are at risk of melting/failure. However the pipes are accessibile for rapid flaw detection and repair, and would be able to be repaired quickly in the case of a fire assuming parts were available. | 0
1 | Force of flood waters | 💦🌊 | ✅ Yes | Moderate Impact | The concrete construction (armoring and strengthening) and burying of the ABR, mean force of flood waters will have minimal impact when located away from rivers or coastal areas. If inlet pipes are not secured or buried, they may present a risk of failure. If the system is partially exposed to flood water, such as on the river bank or coastline, flood waters are more of a concern. | 1
1 | Increased inflow velocity | 💦🌊 | ✅ Yes | Moderate Impact | If the pressure head for the treatment is high and/or inflow velocity is hight, the residence time in various chambers will be reduced, reducing treatment effectiveness. | 1
1 | Increased inflow volume | 💦🌊 | ✅ Yes | Moderate Impact | If the pressure head for the treatment is high and/or inflow velocity is hight, the residence time in various chambers will be reduced, reducing treatment effectiveness. | 1
1 | Increased levels of receiving waterways | 💦 | ✅ Yes | Moderate Impact | Backflow or restricted discharge due to raised receiving water levels could reduce residence time and function of the ABR = low impact. Extended periods and flat terrain could cause backflow to the toilet = medium impact. Overall in Banjarmasin this is medium impact as it is quite likely and very flat. | 1
1 | Reduced inflow velocity | 🌵 | ✅ Yes | Low Impact | A regular flow of water drives flows through the ABR. Reduced velocity is ok, it will increase the pathogen treatment time in each chamber. | 0
1 | Reduced inflow volume | 🌵 | ✅ Yes | Moderate Impact | Reduced water inflow volumes may mean an increase in pathogen concentration in the chambers (less diultion). It's likely the ABR can buffer and reductions in flow volume and increase in pathogen concentration through a longer treatment time because of the reduced flows. Water is required to move waste from toilets to ABR to be treated, so as long as water volume is not below these required levels, impacts will be lower. | 1
1 | Rise in groundwater level and/or groundwater saturation | 💦🌧🌊 | ✅ Yes | Moderate Impact | The ABR is deployed in an area of high groundwater and is/will be subject, flooding, high rainfall and coastal inundation. The concrete construction (armouring and strengthening) likely provides some mitigation to buoyancy forces. However, because it is buried and the nature of the hazard/CIDs there is still potential for moderate impact. | 1
0 | Temperature driven expansion/contraction of materials | 🔥🌡☀️ | ⛔️ No |  |  | 0
1 | Uprooting by fallen trees | 💨 | ✅ Yes | Low Impact | It's unlikely uprooted trees would impact the ABR as an excavated site is necessary for its installation. This would only be an issue if trees grew over time and roots were adjacent/under components | 0
1 | Variable inflow velocity | 🌧 | ✅ Yes | Low Impact | Variable inflow velocity (low and high) can be accommodated by the ABR to a point. Refer to comments above on high flows. | 0
1 | Variable inflow volume | 🌧 | ✅ Yes | Low Impact | Variable inflow volume (low and high) can be accommodated by the ABR to a potint. Refer to comments above on high flows. | 0
1 | Water ingress / inundation | 💦🌊 | ✅ Yes | High Impact | If the pressure head for the treatment is high and/or inflow velocity is high, the residence time in various chambers will be reduced, reducing treatment effectiveness. | 1
1 | Wind force on sanitation structures | 💨 | ✅ Yes | Low Impact | The ABR is buried and heavy, wind is unlikely to impact the structure. | 0
1 | Wind-blown debris | 💨 | ✅ Yes | Low Impact | The technology is buried underground so that windblown debris damage is less likely. Depending on location of pipes, they could be struck by debris or debris clogging inlet, but this is lower risk | 0
1 | Biological organisms exposed to saltwater | 🌊 | ✅ Yes | Moderate Impact | Would have less BOD removal and less pathogen removal, but the ABR would still function in terms of physical flow | 1
1 | Changes in pathogen concentration in inflow | 💦🌵 | ✅ Yes | Moderate Impact | The ABR would be able to reduce pathogens, but if the concentration became very high or if there were a cholera outbreak, the effluent may be poor quality | 1
1 | Extreme heat | 🌡☀️ | ✅ Yes | Low Impact | Extreme heat would have little affect on the structure and treatment processes which are insulated underground | 0
0 | Variation in inflow or storage temperature | 🌡☀️ | ⛔️ No |  |  | 0
1 | Reduced dilution capacity of receiving waters | 🌵 | ✅ Yes | Moderate Impact | Given the system discharges to the waterway and no soak pit (from the scoping tab) the discuarge of this effluent to stressed waterways may become forbidden. Heat stress causing low river flow also increases impact of effluent compared with high flow periods | 1
1 | Disrupted access to sanitation technology for O&M | 💦🌊🔥💨 | ✅ Yes | Moderate Impact | If maintenance is needed, such as removing a blockage, the technology would fail without the maintenance people being able to access the technology. As sludge removal is irregular, this is unlikely to be an issue except in a severe incident where emergency maintenance was needed. | 1
1 | Disrupted access to the sanitation technology for major repairs | 💦🌊🔥💨 | ✅ Yes | High Impact | If a blockage causes the ABR to be unable to receive new waste, the technology would not be able to be used at all until it can be access for maintenance | 1
1 | Disrupted electricity inputs to the sanitation technology | 💦🌊🔥💨☀️ | ✅ Yes | Low Impact | The technology does not rely on electricity. It is assumed that sewage is fed into the ABR via gravity. | 0
1 | Disrupted faecal sludge emptying services | 💦🌊🔥💨 | ✅ Yes | Moderate Impact | Depending how badly the ABR needs desludging, performance could be degraded to different levels | 1
1 | Disrupted water inputs to the sanitation technology | 💦🌊🔥💨🌵 | ✅ Yes | High Impact | Faecal waste cannot be moved from the toilet to the ABR without water | 1
Example
| Increased flow velocity | 💦🌊 | ✅ Yes | Low Impact | Technology is raised on a slab, design guidelines recommend placing away from floodplain. Armouring is incorporated as superstructure is a shipping container mitigating flood water force and inundation. Unsealed electrical equipment remains vulnerable to inundation.
Note on D21: An 8m3 mass of soil containing small rocks slides down a slope and into the sanitation technology
Note on D22: Corrosion of parts exposed to saltwater or higher concentrations of waste during low flows happens two times faster than under normal conditions
Note on D23: Water or wind force that causes 30cm of topsoil to be removed at the base of the technology at one side
Note on D24: Due to changes in temperature or moisture, the soil under the sanitation technology or in which the sanitation technology is buried undergoes daily and annual cyclic expansions and contractions
Note on D25: Low intensity fire where flame height reaches 60cm. Heat intense enough to scorch trees but not to the extent that trees will carry fire.
Note on D26: Enough flowing water to knock an adult over or cause a car to lose traction (i.e. ~10cm of flowing water)
Note on D27: Where sewers or pipes are used, a day's peak inflow velocity is triple the average daily inflow velocity due to increased usage, flushing or water ingress during wet periods
Note on D28: A day's inflow volume is triple the average daily inflow volume due to increased usage, flushing or water ingress during wet periods
Note on D29: Where the sanitation technology discharges to a waterway, the waterway rises by 1m
Note on D30: Where sewers or pipes are used, the day's lowest inflow velocity is only 20% of the average daily inflow velocity due to decreased usage, flushing or water ingress during dry periods
Note on D31: The day's inflow volume is only 20% of the daily average inflow volume due to decreased usage, flushing, or water ingress during dry periods
Note on D32: Groundwater table rises to within 0.5m of the ground surface (potential to create water ingress or buoyancy force)
Note on D33: Diurnal air temperature (variation in daily temperature) is 20⁰C
Note on D34: Fallen tree uproots sewers or pipes within 60cm of the ground surface
Note on D35: Where sewers or pipes are used, average monthly inflow velocity in the wet season is 40% higher than the dry season due to changes in usage, flushing and water ingress
Note on D36: Average monthly inflow volume in the wet season is 40% higher than the dry season due to changes in usage, flushing and water ingress
Note on D37: Any water ingress that may occur to the sanitation technology due to groundwater saturation and 30cm height of standing floodwater (potential for water damage, overflow, and excess siltation)
Note on D38: Category 1 tropical cyclone: Sustained windspeeds of 63-88kph and gusts of 91-125 kph
Note on D39: A 50kg tree branch breaks off and falls on the sanitation technology
Note on D40: During a storm surge, seawater reaches outlet pipes or manholes
Note on D41: Pathogen concentration varies by 50% across seasons
Note on D42: Five or more consecutive days of prolonged heat in which the daily maximum temperature is higher than the average maximum temperature by 5 °C or more (potential to affect biological treatment processes)
Note on D43: Inflow temperature changes by +/- 15⁰C over average expected inflow temperature
Note on D44: Where the sanitation technology discharges to a waterway, the waterway lowers by 1m
Note on D45: Operators and technicians cannot access the sanitation technology for operations and small, routine repairs for 3 days
Note on D46: The sanitation technology cannot be accessed for 3 days to repair major breakage (whichever major breakage is most likely to occur)
Note on D47: External electricity cut off for 7 days
Note on D48: Faecal sludge emptying services cannot desludge the sanitation technology for 3 days when desludging is needed
Note on D49: Normal amounts of external water inputs used for operating the sanitation technology are cut off for 7 days
Note on E19: Filter by HET to see only hazards that are relevant to that HET
Note on G19: If the sanitation technology is exposed to the specfic example of the hazard, how severe will the impact be? Low = Little or no impact on the sanitation technology Moderate = Moderate impact causing reduced performance High = High impact likely causing a failure of the sanitation technology
Note on H19: Why was the low, moderate or high impact rating given?

## 4. Design features
| 4 | Design Features | Step 4: Assess the extent to which the sanitation technology incorporates resilient design features. |  |  |  | Selected HETs
💦 Floods
🌧 Changing precipitation patterns
🌊 High sea level
🔥 Fire weather
💨 Severe wind
🌵 Drought
🌡 Changing air temperature
☀️ Extreme heat
Instructions - For each design feature: (An example is provided at the bottom of the page. Hover over the cells or refer to the accompanying guidelines for more details.) 1) Read the design feature description (see accompanying guidelines for more details). 2) Consider if the design feature is reflected (✅ Yes, ⛔️ No) in the sanitation technology design. If yes, describe how the sanitation technology utilises this design feature to accommodate the climate hazards from step 3. 3) If the design feature is not included or is a weak point, identify any possible climate risks (referring back to step 3) due to this. 4) Reflect on potential improvements to increase the climate resilience of the sanitation technology with regard to the design feature.
| Relevant Design Feature |  |  | Design feature integrated? | Description of design feature in the sanitation technology | Climate related risks | Potential Improvements
1. Avoiding exposure to hazards Features that reduce the likelihood that critical components of the sanitation technology become directly exposed to a climate hazard.
1 |  | Raising Raising the technology or critical components so they are less likely to come into contact with floodwater/groundwater. | 💦 🌧 🌊 | ⛔️ No |  | These systems are typically at the low point of an area to allow gravity flow. Raising the roof or manhole lids may be possible but would add challenges to maintenance and the value is questionable.
1 |  | Burying Installing the technology or its components underground so that they are less likely to come into contact with wind pressure, fire, or force of flooding. | 💦 🌊🔥💨 | ✅ Yes | The ABR and pipes are buried underground ~ 2 metres. This protects it from force of flood waters, wave/tidal forces, wind and exposure to fire.
1 |  | Portability The ability of the technology to be easily moved to a new location to avoid exposure to a disturbance (Conversely, portability can also enable the technology to be easily deployed to emergency contexts). | 💦 🌧 🌊🔥💨🌵 | ⛔️ No |  | If incoming hazards are likely to damage or disrupt the ABR, there is no practical way to move it out of harm's way
1 |  | No/low Inputs Technologies that require little or no inputs (e.g. electricity, water, human operators) to operate, thus reducing the need for inputs that could be exposed to disturbances. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | ✅ Yes | No requirements for electricity No requirements for water beyond the 'normal' inputs from toilets Limited/irregular maintenance requirements (sludge pumping)
1 | 2. Withstanding exposure to hazards Features that enable the sanitation technology to resist a climate hazard. The sanitation technology continues to function “as normal” (i.e. no changes in hardware or operations) even when exposed to climate hazards.
1 |  | Armouring and Strengthening Hardening or stiffening the technology or its components against an expected force. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | ✅ Yes | Concrete constrution, 20cm thick walls. The concrete will resist against forces from water, wind and fire. | It's possible it could crack under soil expanision and contraction, or through heavy traffic on the surface of the ABR. It's unknown what level of soil expanision/contraction would do this, however, ensuring it's installed in unreactive soils would help. These systems are may be located at the edge of a waterway (i.e. river bank) or natural low point in an area (i.e. on coast). It is therefore prone to impact of floodwaters (possibly storm surge in other locations if located at the beach) and may require extra armoring in these contexts. | The strength of the armouring and strengthening is also dependent on the quality of the concrete (e.g. rebar, water quality, concrete mix) and installation. As it's not pre-fabricated it's dependent on the skills/diligence of the installer. Pre-fabricated concrete modules could achieve armouring and reduce this risk, however, it comes with transport challenges (and also means local masons are not involved in construction). As per 'weak point' comment, extra armoring may be relevant if located adjacent to a waterway or coastal area.
1 |  | Oversizing Increasing the tolerance or capacity of the technology or its component so that it can accommodate extreme conditions, projected changes in conditions, or changes in number of users. | 💦 🌧 🌊🌵 | ⛔️ No |  | The ABR is designed for 20L/capita/day and has a peak design factor of 4. Once installed in a place it is difficult to expand. It has some capacity to cope with 'spikes' in usage. However, prolonged usage or a permanent increase in the number of users will mean it reaches it's capacity. | Increasing the buffer capacity of the first chamber may be an option if there is adequate space. Allowing space for additional buffer chambers to be added to the end may be a consideration in the siting of the ABR
1 |  | Shapes that distribute pressure The shape of the technology creates more uniform distribution of stress over its cross-section, thus reducing the risk of failure at weaker points. | 💦 🌧 🌊💨🌵 🌡 | ⛔️ No |  | The square shape could be problematic with tidal/wave/flood forces on edges. | For ABRs that are located on the edge of a waterway the shape could ensure there are no edges/protrusions in the waterway that could create increased pressuring during high river flows.
1 |  | Circumvention Technology materials or designs that allow wind or water to pass through so that the stress on the technology or component is reduced. | 💦 🌧 🌊💨 | ⛔️ No
1 |  | Sealing and Barriers Integrating seals, barriers or other forms of protection into the technology to protect critical components or processes from being disrupted by a hazard. | 💦 🌧 🌊🔥🌡☀️ | ✅ Yes | Sealed inlet chambers, and manholes. If properly constructed, inlet chambers and manholes will prevent ingress from floodwater/seawater entering the ABR | The outlet is not sealed, so backflow is possible when water levels are high | You could install a non-return valve on the outlet to prevent backflow from entering chambers Screens for input could reduce clogging from solid waste or other debris. This may also introduce another failure point and also introduces another level of maintenance moving potential downstream failure (clogging over time) upstream (more shorter term challenges such as blocked screens).
1 | 3. Enabling flexibility Features that enable the ST to be adapted or reconfigured, or have its operation changed, in order to continue providing services when exposed to climate hazards.
1 |  | Adaptability The technology design can be adapted or upgraded easily to function better under the changing environmental conditions (e.g. increasingly wet or increasingly dry conditions). | 💦 🌧 🌊🔥💨🌵 🌡☀️ | ⛔️ No |  | The technology needs a minimum amount of water to ensure it can flow between chambers. Reductions in water supply (e.g. drought) would likely reduce water flow potentially reducing it's functionality. Adaptability in this regard is not integrated into the design. It would require some user intervention. In times of increasing flood or rainfall, there may be additional water inputs into the ABR. If retention times were too fast, this would compromise the level of treatment. Discharge to a soak pit (not detailed in the design) could reduce the impact of backflow from raised receiving water levels and may reduce impact on waterway quality during drought periods when dilution capacity of waterways are reduced. | Effluent could be recirculated through the ABR in times of low water. This would require a pumping system which adds cost and complexity to the design. A shut off valve or similar may be useful in times of flood, sea inundation or high rain if water ingreess into the ABR is an issue.
1 |  | Modular design Additional modules can be added (plug-in type model) or removed to increase or decrease capacity of the system to accommodate variability in demand and environmental conditions. | 💦 🌧 🔥💨🌵 | ⛔️ No |  | Module elements (e.g. additional chambers) to the ABR can not be easily removed or bypassed, however could be added if there was space at either end or possibly piped to additional baffles nearby. However, adding on extra modules is not a common practice. | The concrete structure makes removing modules difficult. Providing pipe fitting or junction boxes at the start or end would ease future modifications, as would allowing additional space for more buffers or a parallel systems in the site selection
1 |  | Platform design The technology shares components with other similar technologies, which makes it easier to transition between technologies to suit customer demand or prevailing environmental conditions. | 💦 🌧 🌊🔥💨 | ⛔️ No
1 |  | Redundancy and diversity The technology has redundant components that work in parallel, or that act as back-ups to each other, so that if a component(s) fails, the back-up component can take its place and allow the technology to continue functioning. Diversity entails that the redundant / back-up components can perform the same function, but in a different way. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | ✅ Yes | Multiple settlement and ABR chambers. If one chamber fails, the other chamber/s will provide a level of treatment. | A failure of one chamber will reduce treatment capability (though not result in total loss of treatment)
1 |  | Signalling The technology, by the nature of how it functions or by intentional design, has a way of signalling to operators or users when the technology requires modification to prevent failure or to enhance its performance. | 💦 🌧 🌊🔥💨🌵 ☀️ | ⛔️ No |  | It's difficult to know if there are issues until the technology is already having major issues (e.g. toilets can't be flushed). Difficult to know if effluent is being treated adequately. | Remote flow sensing, or flow analogue gauge of flow rates through inlets, chambers and outlets would indicate if the ABR was failing.
1 | 4. Containing failures Features that enable the sanitation technology to continue providing basic services and meet user needs despite damage to technology components caused by climate hazards.
1 |  | Frangibility Less essential components of the technology are designed to breakaway or fail when exposed to a certain level of pressure to protect more essential components of the technology. | 💦 🌊🔥💨 | ⛔️ No
1 |  | Fail-operational The technology can still provide its overall function even when components or processes are damaged/compromised and undergoing repair. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | ⛔️ No |  | This depends on the degree of damage. It may provide a limited function if damaged (i.e. minor leakage of waste). However, some repairs may require inputs to be stopped or sludge to be removed to access areas for repair. It's not straightforward to isolate chambers. | Options to bypass chambers for repairs when needed may mean the ABR could continue to function while chambers were repaired.
1 |  | Decentralisation Failures in decentralised systems (small-scale individual or clustered systems) are isolated locally which prevents failures from cascading and causing outages to many users/households. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | ✅ Yes | Decentralised technology, may be connected to several households. In the event of a failure, only a limited number of households connected to the ABR will be impacted. Compared to a sewered technology where large #'s of households would be impacted. | Compared to a septic tank, it is still possible that several households will have disrupted sanitation in the event of a failure. The assessment team noted there may be as many as 40 households connected to some ABRs. | Guidelines on maximum number of households to be connected to an ABR.
1 | 5. Limiting consequences of complete failure Features that minimise the negative health and environmental consequences of complete ST failure due to a climate hazard.
1 |  | Safe disposal The materials from the destroyed technology are not toxic to the environment or public health and can be safely disposed. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | ✅ Yes | Materials are concrete, PVC and steel. If destroyed in fire, flood, etc it does not cause environmental pollution beyond the wastewater waste. There are not materials that would leach into groundwater or create other adverse public health affects.
1 |  | Reusable materials The materials from the destroyed technology can be reused for other purposes (including rebuilding the technology). | 💦 🌧 🌊🔥💨🌵 🌡☀️ | ⛔️ No |  | The broken concrete is generally not easily used for other purposes. | If the chambers were built out of bricks, they could potentially be recovered and used for other purposes.
1 |  | Fail-silence The technology stops operating if a critical failure is detected, hence preventing the release of human waste into the environment. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | ✅ Yes | Waste is held in the tank until it dries out if the ST stops operating which does not pose a continual health risk |  | Could consider HDPE linings around the outside of the ABR to limit public health risks in the event of leakage/damage.
1 | 6. Facilitating fast recovery Features that enable the ST to be quickly rebuilt or restored if they are damaged, disrupted or destroyed by a climate hazard.
1 |  | Repair speed The technology, its components, processes, or its operations can be quickly replaced, rebuilt or restored if destroyed or disrupted so that performance downtime or degradation is minimised. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | ✅ Yes | Locally available materials Simple construction. If the ABR is physically damaged, it is likely that repairs could be done by local labour using local materials.
1 |  | Accessibility for rapid flaw detection Components or processes of the technology can be easily accessed for examination. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | ✅ Yes | Access hatch for repairs. The chambers can be easily accessed for repairs from the ground. | Access to some chambers may be difficult if full of sludge or water. This will also present a health risk to those doing repairs. There is also no way to shut off continued use during repairs. | Introduce shut off valve and ways to shut off toilets that feed into the ABR as needed. As noted earlier, the ability to bypass certain chamers would also help in repairing one chamber while others continue to function. A 'repair' procedure and required tools/equipment should be provided with each ABR, and ideally ABRs should only be installed where trained personnel are available to conduct repairs safely.
1 | 7. Providing benefits beyond resilience Features that enable the sanitation technology to provide other benefits to people or to other systems that aid in broader community or system resilience.
1 |  | Reciprocity By providing its service, the technology produces outputs that build resilience in, or aid, another on-site or off-site system. |  | ⛔️ No |  |  | If a soak pit or leach field was incorporated into the design, it could incorporate plantings to provide other functionality (e.g. animal feed), assuming it could be done without public health risk.
1 |  | Hybridising Unrelated systems or technologies share the same physical space or structure, thus saving space and enhancing opportunities for reciprocity. |  | ✅ Yes | Surface can be used as a road/hard surface
1 |  | Transformative capacity The technology provides an additional service(s) beyond its usual intent that further aids resilient communities. |  | ⛔️ No
Example
|  | Sealing and barriers Integrating seals, barriers or other forms of protection into the technology to protect critical components or processes from being disrupted by a hazard. |  | ✅ Yes | Holding tank non-return prevents backflow into toilet in flood. Sealable treatment area door prevents flood inundation. Electrics are sealed and can sustain temporary flood inundation. Roof eaves & insulation mitigate high temps by protecting equipment and supporting thermal comfort in toilet area. | In floods, the absence of sealing in the toilet areas poses a risk of floodwater ingress into treatment system. | A sealable door to the toilet area could be installed at low cost to seal this area against flood inundation.
Note on F18: If the design feature is reflected in the sanitation technology design in any way that supports resilience, select yes and describe it in the next column.
Note on G18: If the design feature is reflected in the sanitation technology design, describe how it helps accommodate climate hazards
Note on H18: If the design feature is absent or a weak point, how does this compromise the sanitation technology's climate resilience? Note: Answering this question is optional. Some features are not relevant to a sanitation technology, or not integrated to avoid over-design. Leave blank if n/a or no ideas.
Note on I18: How could the climate resilience of the sanitation technology be improved through incorporating this design feature? Leave blank if n/a or no ideas.

## 5. Overall resilience
| 5 | Overall resilience self-assessment | [6 empty] | Step 5: Consider the overall resilience of your technology to each hazardous event and trend.
Instructions - for each hazardous event or trend: 1) Look at the overall impact rating that is auto-calculated based on the proportion of low, moderate, and high impact ratings you provided in step 3. 2) Give an overall resilience rating. You may refer back to step 3 and filter the hazards by the 'Hazardous events and trends' (HET) to remind yourself of the likely impacts. 3) Provide a brief justification for your rating.
Hazards Impact
|  |  | Low Impact | Moderate Impact | High Impact | Overall |  | Resilience rating | Justification
|  | Example: Floods | 60% | 20% | 20% | 30.4% | Low impact | High Resilience | The superstructure, combined with the raising of the ST 1 metre above ground, and sealed storage tanks supports the ST resilience to floods. However, the ST is not off-grid so functionality could be temporarily impacted in floods.
1 | 💦 | Flood | 7.692% | 69.23% | 23.08% | 57.54% | Moderate Impact | Medium Resilience | The structural integrityof the ABR is resilient to floods, though inlet pipes may be disturbed if not buried. A risk for floods is inundation/increased flow into chambers reducing retention time and treatment effectiveness. It could also "blow" manholes and lead to pollution.
1 | 🌧 | Changing Precipitation Patterns | 75% | 25% | 0% | 13.25% | Low Impact | High Resilience | The ABR is able to buffer changes in precipitation patterns, it is unlikely to create serious impacts.
1 | 🌊 | High Sea Level | 14.29% | 64.29% | 21.43% | 53.5% | Moderate Impact | Low Resilience | Inlet pipes may be disturbed if not buried. Inundation/increased flow into chambers reducing retention time and treatment effectiveness. It could also "blow" manholes and lead to faecal pollution of the environment. Salt water may impact the biota temporarily in the ABR.
1 | 🔥 | Fire Weather | 33.33% | 33.33% | 33.33% | 50% | Moderate Impact | High Resilience | Fires are likely to have a low impact on the main ABR structure as it is concrete and buried. However, fires may impact any exposed inlet pipes, though if they are exposed they would also be easy/fast to repair.
1 | 💨 | Severe Wind | 50% | 25% | 25% | 37.75% | Moderate Impact | High Resilience | Winds are considered low risk for the ABR. The main risk from winds is additional debris that may enter the system though this is unlikely as entry points for debris are inside dwellings and into the toilet.
1 | 🌵 | Droughts | 28.57% | 57.14% | 14.29% | 43% | Moderate Impact | Medium Resilience | Droughts may reduce the water available for flushing needed to move faecal/sewage into the ABR. Droughts would likely not impact the treatment efficacy as it would lead to increased residence time in the treatment train. Doughts would also reduce the dilution at any discharge points/waters
1 | 🌡 | Changing Air Temperature | 100% | 0% | 0% | 1% | Low Impact | High Resilience | Changes in air temperature are unlikely to have any impacts on the ABR. They may cause some fluctuations in the treatment processes, these would be expected to be minor in this location
1 | ☀️ | Extreme Heat | 100% | 0% | 0% | 1% | Low Impact | High Resilience | Extreme heat is unlikely to have any impacts on the ABR. Events may cause some fluctuations in the treatment processes, these would be expected to be minor.
Note on E6: Calculated automatically from responses in step 3
Note on E7: % hazards with low impact on sanitation technology
Note on F7: % hazards with moderate impact on sanitation technology
Note on G7: % hazards with high impact on sanitation technology
Note on H7: Calculated automatically from responses in step 3
Note on H8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hide column
Note on J7: Overall, how resilient is the sanitation technology against the hazardous event or trend? Low Resilience = Likely to fail or have extended outage; Medium resilience = reduced sanitation technology performance or temporary outage; High resilience = continues to function
Note on K7: Why was the low, medium or high rating given?

## Overall report
Sanitation Technology Climate Resilience Summary
| Hazardous event or trend |  |  | Impact Rating |  | Resilience Rating
| Column1 | Column2 | Column3 | Column32 | Column4 | Column10 | Column13
1 | 💦 | Flood |  | Moderate Impact |  | Medium Resilience
1 |  | The structural integrityof the ABR is resilient to floods, though inlet pipes may be disturbed if not buried. A risk for floods is inundation/increased flow into chambers reducing retention time and treatment effectiveness. It could also "blow" manholes and lead to pollution.
1 | 🌧 | Changing precipitation patterns |  | Low Impact |  | High Resilience
1 |  | The ABR is able to buffer changes in precipitation patterns, it is unlikely to create serious impacts.
1 | 🌊 | High sea level |  | Moderate Impact |  | Low Resilience
1 |  | Inlet pipes may be disturbed if not buried. Inundation/increased flow into chambers reducing retention time and treatment effectiveness. It could also "blow" manholes and lead to faecal pollution of the environment. Salt water may impact the biota temporarily in the ABR.
1 | 🔥 | Fire weather |  | Moderate Impact |  | High Resilience
1 |  | Fires are likely to have a low impact on the main ABR structure as it is concrete and buried. However, fires may impact any exposed inlet pipes, though if they are exposed they would also be easy/fast to repair.
1 | 💨 | Severe wind |  | Moderate Impact |  | High Resilience
1 |  | Winds are considered low risk for the ABR. The main risk from winds is additional debris that may enter the system though this is unlikely as entry points for debris are inside dwellings and into the toilet.
1 | 🌵 | Droughts |  | Moderate Impact |  | Medium Resilience
1 |  | Droughts may reduce the water available for flushing needed to move faecal/sewage into the ABR. Droughts would likely not impact the treatment efficacy as it would lead to increased residence time in the treatment train. Doughts would also reduce the dilution at any discharge points/waters
1 | 🌡 | Changing air temperature |  | Low Impact |  | High Resilience
1 |  | Changes in air temperature are unlikely to have any impacts on the ABR. They may cause some fluctuations in the treatment processes, these would be expected to be minor in this location
1 | ☀️ | Extreme heat |  | Low Impact |  | High Resilience
1 |  | Extreme heat is unlikely to have any impacts on the ABR. Events may cause some fluctuations in the treatment processes, these would be expected to be minor.

## Impact report
Impactful Hazards
Potential Hazard | Impact Rating | Justification
Corrosion | Moderate Impact | The ABR is deployed in an area of high groundwater and is/will be subject, flooding, high rainfall and coastal inundation. The concrete construction (armouring and strengthening) likely provides some mitigation to buoyancy forces. However, because it is buried and the nature of the hazard/CIDs there is still potential for moderate impact. | The ABR is deployed in an area of high groundwater and is/will be subject, flooding, high rainfall and coastal inundation. The concrete construction (armouring and strengthening) likely provides some mitigation to buoyancy forces. However, because it is buried and the nature of the hazard/CIDs there is still potential for moderate impact.
Erosion | Moderate Impact | Salt water from coastal flooding could corrode the rebar in the ABR, weakening it over time. Corrosion will be difficult to observe as rebar is not exposed. | Salt water from coastal flooding could corrode the rebar in the ABR, weakening it over time. Corrosion will be difficult to observe as rebar is not exposed.
Force of flood waters | Moderate Impact | The concrete construction (armoring and strengthening) and burying of the ABR, mean force of flood waters will have minimal impact when located away from rivers or coastal areas. If inlet pipes are not secured or buried, they may present a risk of failure. If the system is partially exposed to flood water, such as on the river bank or coastline, flood waters are more of a concern. | The concrete construction (armoring and strengthening) and burying of the ABR, mean force of flood waters will have minimal impact when located away from rivers or coastal areas. If inlet pipes are not secured or buried, they may present a risk of failure. If the system is partially exposed to flood water, such as on the river bank or coastline, flood waters are more of a concern.
Increased inflow velocity | Moderate Impact | If the pressure head for the treatment is high and/or inflow velocity is hight, the residence time in various chambers will be reduced, reducing treatment effectiveness. | If the pressure head for the treatment is high and/or inflow velocity is hight, the residence time in various chambers will be reduced, reducing treatment effectiveness.
Increased inflow volume | Moderate Impact | If the pressure head for the treatment is high and/or inflow velocity is hight, the residence time in various chambers will be reduced, reducing treatment effectiveness. | If the pressure head for the treatment is high and/or inflow velocity is hight, the residence time in various chambers will be reduced, reducing treatment effectiveness.
Increased levels of receiving waterways | Moderate Impact | Backflow or restricted discharge due to raised receiving water levels could reduce residence time and function of the ABR = low impact. Extended periods and flat terrain could cause backflow to the toilet = medium impact. Overall in Banjarmasin this is medium impact as it is quite likely and very flat. | Backflow or restricted discharge due to raised receiving water levels could reduce residence time and function of the ABR = low impact. Extended periods and flat terrain could cause backflow to the toilet = medium impact. Overall in Banjarmasin this is medium impact as it is quite likely and very flat.
Reduced inflow volume | Moderate Impact | Reduced water inflow volumes may mean an increase in pathogen concentration in the chambers (less diultion). It's likely the ABR can buffer and reductions in flow volume and increase in pathogen concentration through a longer treatment time because of the reduced flows. Water is required to move waste from toilets to ABR to be treated, so as long as water volume is not below these required levels, impacts will be lower. | Reduced water inflow volumes may mean an increase in pathogen concentration in the chambers (less diultion). It's likely the ABR can buffer and reductions in flow volume and increase in pathogen concentration through a longer treatment time because of the reduced flows. Water is required to move waste from toilets to ABR to be treated, so as long as water volume is not below these required levels, impacts will be lower.
Rise in groundwater level and/or groundwater saturation | Moderate Impact | The ABR is deployed in an area of high groundwater and is/will be subject, flooding, high rainfall and coastal inundation. The concrete construction (armouring and strengthening) likely provides some mitigation to buoyancy forces. However, because it is buried and the nature of the hazard/CIDs there is still potential for moderate impact. | The ABR is deployed in an area of high groundwater and is/will be subject, flooding, high rainfall and coastal inundation. The concrete construction (armouring and strengthening) likely provides some mitigation to buoyancy forces. However, because it is buried and the nature of the hazard/CIDs there is still potential for moderate impact.
Water ingress / inundation | High Impact | If the pressure head for the treatment is high and/or inflow velocity is high, the residence time in various chambers will be reduced, reducing treatment effectiveness. | If the pressure head for the treatment is high and/or inflow velocity is high, the residence time in various chambers will be reduced, reducing treatment effectiveness.
Biological organisms exposed to saltwater | Moderate Impact | Would have less BOD removal and less pathogen removal, but the ABR would still function in terms of physical flow | Would have less BOD removal and less pathogen removal, but the ABR would still function in terms of physical flow
Changes in pathogen concentration in inflow | Moderate Impact | The ABR would be able to reduce pathogens, but if the concentration became very high or if there were a cholera outbreak, the effluent may be poor quality | The ABR would be able to reduce pathogens, but if the concentration became very high or if there were a cholera outbreak, the effluent may be poor quality
Reduced dilution capacity of receiving waters | Moderate Impact | Given the system discharges to the waterway and no soak pit (from the scoping tab) the discuarge of this effluent to stressed waterways may become forbidden. Heat stress causing low river flow also increases impact of effluent compared with high flow periods | Given the system discharges to the waterway and no soak pit (from the scoping tab) the discuarge of this effluent to stressed waterways may become forbidden. Heat stress causing low river flow also increases impact of effluent compared with high flow periods
Disrupted access to sanitation technology for O&M | Moderate Impact | If maintenance is needed, such as removing a blockage, the technology would fail without the maintenance people being able to access the technology. As sludge removal is irregular, this is unlikely to be an issue except in a severe incident where emergency maintenance was needed. | If maintenance is needed, such as removing a blockage, the technology would fail without the maintenance people being able to access the technology. As sludge removal is irregular, this is unlikely to be an issue except in a severe incident where emergency maintenance was needed.
Disrupted access to the sanitation technology for major repairs | High Impact | If a blockage causes the ABR to be unable to receive new waste, the technology would not be able to be used at all until it can be access for maintenance | If a blockage causes the ABR to be unable to receive new waste, the technology would not be able to be used at all until it can be access for maintenance
Disrupted faecal sludge emptying services | Moderate Impact | Depending how badly the ABR needs desludging, performance could be degraded to different levels | Depending how badly the ABR needs desludging, performance could be degraded to different levels
Disrupted water inputs to the sanitation technology | High Impact | Faecal waste cannot be moved from the toilet to the ABR without water | Faecal waste cannot be moved from the toilet to the ABR without water

## Strengths report
Design Feature Strengths
Integrated Design Feature |  | Description
Burying | Installing the technology or its components underground so that they are less likely to come into contact with wind pressure, fire, or force of flooding. | The ABR and pipes are buried underground ~ 2 metres. This protects it from force of flood waters, wave/tidal forces, wind and exposure to fire.
No/low inputs | Technologies that require little or no inputs (e.g. electricity, water, human operators) to operate, thus reducing the need for inputs that could be exposed to disturbances. | No requirements for electricity No requirements for water beyond the 'normal' inputs from toilets Limited/irregular maintenance requirements (sludge pumping)
Armouring and Strengthening | Hardening or stiffening the technology or its components against an expected force. | Concrete constrution, 20cm thick walls. The concrete will resist against forces from water, wind and fire.
Sealing and barriers | Integrating seals, barriers or other forms of protection into the technology to protect critical components or processes from being disrupted by a hazard. | Sealed inlet chambers, and manholes. If properly constructed, inlet chambers and manholes will prevent ingress from floodwater/seawater entering the ABR
Redundancy and dive | The technology has redundant components that work in parallel, or that act as back-ups to each other, so that if a component(s) fails, the back-up component can take its place and allow the technology to continue functioning. Diversity entails that the redundant / back-up components can perform the same function, but in a different way. | Multiple settlement and ABR chambers. If one chamber fails, the other chamber/s will provide a level of treatment.
Decentralisation | Failures in decentralised systems (small-scale individual or clustered systems) are isolated locally which prevents failures from cascading and causing outages to many users/households. | Decentralised technology, may be connected to several households. In the event of a failure, only a limited number of households connected to the ABR will be impacted. Compared to a sewered technology where large #'s of households would be impacted.
Safe disposal | The materials from the destroyed technology are not toxic to the environment or public health and can be safely disposed. | Materials are concrete, PVC and steel. If destroyed in fire, flood, etc it does not cause environmental pollution beyond the wastewater waste. There are not materials that would leach into groundwater or create other adverse public health affects.
Fail-silence | If the technology fails so that it cannot be used anymore, no failure will pose a continual health risk to the public or the environment beyond making the technology unavailable for use. | Waste is held in the tank until it dries out if the ST stops operating which does not pose a continual health risk
Repair speed | The technology, its components, processes, or its operations can be quickly replaced, rebuilt or restored if destroyed or disrupted so that performance downtime or degradation is minimised. | Locally available materials Simple construction. If the ABR is physically damaged, it is likely that repairs could be done by local labour using local materials.
Accessibility for rapid flaw detection and repair | Components or processes of the technology can be easily accessed for examination. | Access hatch for repairs. The chambers can be easily accessed for repairs from the ground.
Hybridising | Unrelated systems or technologies share the same physical space or structure, thus saving space and enhancing opportunities for reciprocity. | Surface can be used as a road/hard surface

## Improvements report
Design Feature Improvements
Design Feature |  | Climate Related Risks | Improvements
Armouring and Strengthening | Hardening or stiffening the technology or its components against an expected force. | It's possible it could crack under soil expanision and contraction, or through heavy traffic on the surface of the ABR. It's unknown what level of soil expanision/contraction would do this, however, ensuring it's installed in unreactive soils would help. These systems are may be located at the edge of a waterway (i.e. river bank) or natural low point in an area (i.e. on coast). It is therefore prone to impact of floodwaters (possibly storm surge in other locations if located at the beach) and may require extra armoring in these contexts. | The strength of the armouring and strengthening is also dependent on the quality of the concrete (e.g. rebar, water quality, concrete mix) and installation. As it's not pre-fabricated it's dependent on the skills/diligence of the installer. Pre-fabricated concrete modules could achieve armouring and reduce this risk, however, it comes with transport challenges (and also means local masons are not involved in construction). As per 'weak point' comment, extra armoring may be relevant if located adjacent to a waterway or coastal area.
Oversizing | Increasing the tolerance or capacity of the technology or its component so that it can accommodate extreme conditions, projected changes in conditions, or changes in number of users. | The ABR is designed for 20L/capita/day and has a peak design factor of 4. Once installed in a place it is difficult to expand. It has some capacity to cope with 'spikes' in usage. However, prolonged usage or a permanent increase in the number of users will mean it reaches it's capacity. | Increasing the buffer capacity of the first chamber may be an option if there is adequate space. Allowing space for additional buffer chambers to be added to the end may be a consideration in the siting of the ABR
Shapes that distribute | The shape of the technology creates more uniform distribution of stress over its cross-section, thus reducing the risk of failure at weaker points. | The square shape could be problematic with tidal/wave/flood forces on edges. | For ABRs that are located on the edge of a waterway the shape could ensure there are no edges/protrusions in the waterway that could create increased pressuring during high river flows.
Sealing and barriers | Integrating seals, barriers or other forms of protection into the technology to protect critical components or processes from being disrupted by a hazard. | The outlet is not sealed, so backflow is possible when water levels are high | You could install a non-return valve on the outlet to prevent backflow from entering chambers Screens for input could reduce clogging from solid waste or other debris. This may also introduce another failure point and also introduces another level of maintenance moving potential downstream failure (clogging over time) upstream (more shorter term challenges such as blocked screens).
Adaptability | The technology design can be adapted or upgraded easily to function better under the changing environmental conditions (e.g. increasingly wet or increasingly dry conditions). | The technology needs a minimum amount of water to ensure it can flow between chambers. Reductions in water supply (e.g. drought) would likely reduce water flow potentially reducing it's functionality. Adaptability in this regard is not integrated into the design. It would require some user intervention. In times of increasing flood or rainfall, there may be additional water inputs into the ABR. If retention times were too fast, this would compromise the level of treatment. Discharge to a soak pit (not detailed in the design) could reduce the impact of backflow from raised receiving water levels and may reduce impact on waterway quality during drought periods when dilution capacity of waterways are reduced. | Effluent could be recirculated through the ABR in times of low water. This would require a pumping system which adds cost and complexity to the design. A shut off valve or similar may be useful in times of flood, sea inundation or high rain if water ingreess into the ABR is an issue.
Modular design | Additional modules can be added (plug-in type model) or removed to increase or decrease capacity of the system to accommodate variability in demand and environmental conditions. | Module elements (e.g. additional chambers) to the ABR can not be easily removed or bypassed, however could be added if there was space at either end or possibly piped to additional baffles nearby. However, adding on extra modules is not a common practice. | The concrete structure makes removing modules difficult. Providing pipe fitting or junction boxes at the start or end would ease future modifications, as would allowing additional space for more buffers or a parallel systems in the site selection
Signalling | The technology, by the nature of how it functions or by intentional design, has a way of signalling to operators or users when the technology requires modification to prevent failure or to enhance its performance. | It's difficult to know if there are issues until the technology is already having major issues (e.g. toilets can't be flushed). Difficult to know if effluent is being treated adequately. | Remote flow sensing, or flow analogue gauge of flow rates through inlets, chambers and outlets would indicate if the ABR was failing.
Fail-operational | The technology can still provide its overall function even when components or processes are damaged/compromised and undergoing repair. | This depends on the degree of damage. It may provide a limited function if damaged (i.e. minor leakage of waste). However, some repairs may require inputs to be stopped or sludge to be removed to access areas for repair. It's not straightforward to isolate chambers. | Options to bypass chambers for repairs when needed may mean the ABR could continue to function while chambers were repaired.
Decentralisation | Failures in decentralised systems (small-scale individual or clustered systems) are isolated locally which prevents failures from cascading and causing outages to many users/households. | Compared to a septic tank, it is still possible that several households will have disrupted sanitation in the event of a failure. The assessment team noted there may be as many as 40 households connected to some ABRs. | Guidelines on maximum number of households to be connected to an ABR.
Reusable materials | The materials from the destroyed technology can be reused for other purposes (including rebuilding the technology). | The broken concrete is generally not easily used for other purposes. | If the chambers were built out of bricks, they could potentially be recovered and used for other purposes.
Fail-silence | If the technology fails so that it cannot be used anymore, no failure will pose a continual health risk to the public or the environment beyond making the technology unavailable for use. |  | Could consider HDPE linings around the outside of the ABR to limit public health risks in the event of leakage/damage.
Accessibility for rapid flaw detection and repair | Components or processes of the technology can be easily accessed for examination. | Access to some chambers may be difficult if full of sludge or water. This will also present a health risk to those doing repairs. There is also no way to shut off continued use during repairs. | Introduce shut off valve and ways to shut off toilets that feed into the ABR as needed. As noted earlier, the ability to bypass certain chamers would also help in repairing one chamber while others continue to function. A 'repair' procedure and required tools/equipment should be provided with each ABR, and ideally ABRs should only be installed where trained personnel are available to conduct repairs safely.
Reciprocity | By providing its service, the technology produces outputs that build resilience in, or aid, another on-site or off-site system. |  | If a soak pit or leach field was incorporated into the design, it could incorporate plantings to provide other functionality (e.g. animal feed), assuming it could be done without public health risk.

## Model_Lists (hidden)
Used to store drop down list information
relevent List Options | Rating Options (2) | Rating Options (3) | HazardRisk Options | rating overall | Score Weight | resilience rating | ReportOptions | CIDS | ToggleHazards | OverallScore
Select One | ✅ Yes | Yes | Low |  |  | Low Resilience | Summary | Flood | All hazards for relevant HETs | Low
✅ Yes | ⛔️ No | Middle | Moderate | Low Impact | 0.01 | Medium Resilience | Detailed | Changing Precipitation Patterns | 💦 Floods | Low-Moderate
⛔️ No |  | No | High | Moderate Impact | 0.5 | High Resilience |  | High Sea Level | 🌧 Changing precipitation patterns | Moderate
|  |  |  | High Impact | 0.99 |  |  | Fire Weather | 🏝High sea level | Moderate-High
[8 empty] | Severe Wind | 🔥 Fire weather | High
[8 empty] | Droughts | 🌬 Severe wind
[8 empty] | Changing Air Temperature | 🌵 Drought
[8 empty] | Extreme Heat | 🌡 Changing air temperature
🥵 Extreme heat

## OverView_Calc (hidden)
| Relevant | Rel | Q1 | Score1 | AutoCalc | Q2 | SelfAssessment | Icon | Comment | Hazard Score - Low | Hazard Score - Moderate | Hazard Score - High | Low % | Moderate % | High % | Characteristics
Flood | TRUE | 57.54% | Moderate Impact | 2 | Moderate Impact | Medium Resilience | Medium Resilience | 2 | The structural integrityof the ABR is resilient to floods, though inlet pipes may be disturbed if not buried. A risk for floods is inundation/increased flow into chambers reducing retention time and treatment effectiveness. It could also "blow" manholes and lead to pollution. | 1 | 9 | 3 | 7.692% | 69.23% | 23.08% | Multiple flooding events per year due to fluvial flooding
Changing Precipitation Patterns | TRUE | 13.25% | Low Impact | 1 | Low Impact | High Resilience | High Resilience | 1 | The ABR is able to buffer changes in precipitation patterns, it is unlikely to create serious impacts. | 3 | 1 | 0 | 75% | 25% | 0% | Wet season and dry season with increasing variability due to climate change
High Sea Level | TRUE | 53.5% | Moderate Impact | 2 | Moderate Impact | Low Resilience | Low Resilience | 2 | Inlet pipes may be disturbed if not buried. Inundation/increased flow into chambers reducing retention time and treatment effectiveness. It could also "blow" manholes and lead to faecal pollution of the environment. Salt water may impact the biota temporarily in the ABR. | 2 | 9 | 3 | 14.29% | 64.29% | 21.43% | Not coastal, but rivers are hydrologically connected to the tide, so groundwater and river levels go up with sea level rise. Rivers are brackish.
Fire Weather | TRUE | 50% | Moderate Impact | 2 | Moderate Impact | High Resilience | High Resilience | 2 | Fires are likely to have a low impact on the main ABR structure as it is concrete and buried. However, fires may impact any exposed inlet pipes, though if they are exposed they would also be easy/fast to repair. | 2 | 2 | 2 | 33.33% | 33.33% | 33.33% | Fire risk is mostly driven by human activities, particularly in informal settlements
Severe Wind | TRUE | 37.75% | Moderate Impact | 2 | Moderate Impact | High Resilience | High Resilience | 2 | Winds are considered low risk for the ABR. The main risk from winds is additional debris that may enter the system though this is unlikely as entry points for debris are inside dwellings and into the toilet. | 4 | 2 | 2 | 50% | 25% | 25% | Strong storms are a risk, but cyclones are not a high risk
Droughts | TRUE | 43% | Moderate Impact | 2 | Moderate Impact | Medium Resilience | Medium Resilience | 2 | Droughts may reduce the water available for flushing needed to move faecal/sewage into the ABR. Droughts would likely not impact the treatment efficacy as it would lead to increased residence time in the treatment train. Doughts would also reduce the dilution at any discharge points/waters | 2 | 4 | 1 | 28.57% | 57.14% | 14.29% | Droughts are relatively lower risk compared to floods, but water shortages can occur
Changing Air Temperature | TRUE | 1% | Low Impact | 1 | Low Impact | High Resilience | High Resilience | 1 | Changes in air temperature are unlikely to have any impacts on the ABR. They may cause some fluctuations in the treatment processes, these would be expected to be minor in this location | 2 | 0 | 0 | 100% | 0% | 0% | Not a lot of temperature variability as temperature stay around 20 - 30 degrees annually
Extreme Heat | TRUE | 1% | Low Impact | 1 | Low Impact | High Resilience | High Resilience | 1 | Extreme heat is unlikely to have any impacts on the ABR. Events may cause some fluctuations in the treatment processes, these would be expected to be minor. | 2 | 0 | 0 | 100% | 0% | 0% | Exposed to extreme heat waves and high humidity annually

## DF_Calc (hidden)
| 💦 Floods | 🌧 Changing precipitation patterns | 🌊 High sea level | 🔥 Fire weather | 💨 Severe wind | 🌵 Drought | 🌡 Changing air temperature | ☀️ Extreme heat
| 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
| Flood | Changing Precipitation Patterns | High Sea Level | Fire Weather | Severe Wind | Droughts | Changing Air Temperature | Extreme Heat
User Relevent | ✅ Yes | ✅ Yes | ✅ Yes | ✅ Yes | ✅ Yes | ✅ Yes | ✅ Yes | ✅ Yes | Show In Strengths | Description | Show In Improvements | Climate risks | Improvements | Blurb | String | 💦 Floods | 🌧 Changing precipitation patterns | 🌊 High sea level | 🔥 Fire weather | 💨 Severe wind | 🌵 Drought | 🌡 Changing air temperature | ☀️ Extreme heat
1. Avoiding exposure to hazards
Raising | Yes | Yes | Yes | No | No | No | No | No | FALSE |  | FALSE | These systems are typically at the low point of an area to allow gravity flow. Raising the roof or manhole lids may be possible but would add challenges to maintenance and the value is questionable. |  | Raising the technology or critical components so they are less likely to come into contact with floodwater/groundwater. | 💦 🌧 🌊 | 💦 | 🌧 | 🌊
Burying | Yes | No | Yes | Yes | Yes | No | No | No | TRUE | The ABR and pipes are buried underground ~ 2 metres. This protects it from force of flood waters, wave/tidal forces, wind and exposure to fire. | FALSE |  |  | Installing the technology or its components underground so that they are less likely to come into contact with wind pressure, fire, or force of flooding. | 💦 🌊🔥💨 | 💦 |  | 🌊 | 🔥 | 💨
Portability | Yes | Yes | Yes | Yes | Yes | Yes | No | No | FALSE |  | FALSE | If incoming hazards are likely to damage or disrupt the ABR, there is no practical way to move it out of harm's way |  | The ability of the technology to be easily moved to a new location to avoid exposure to a disturbance. | 💦 🌧 🌊🔥💨🌵 | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵
No/low inputs | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | TRUE | No requirements for electricity No requirements for water beyond the 'normal' inputs from toilets Limited/irregular maintenance requirements (sludge pumping) | FALSE |  |  | Technologies that require little or no inputs (e.g. electricity, water, human operators) to operate, thus reducing the need for inputs that could be exposed to disturbances. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
2. Withstanding exposure to hazards | [8 empty] | FALSE |  | FALSE
Armouring and Strengthening | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | TRUE | Concrete constrution, 20cm thick walls. The concrete will resist against forces from water, wind and fire. | TRUE | It's possible it could crack under soil expanision and contraction, or through heavy traffic on the surface of the ABR. It's unknown what level of soil expanision/contraction would do this, however, ensuring it's installed in unreactive soils would help. These systems are may be located at the edge of a waterway (i.e. river bank) or natural low point in an area (i.e. on coast). It is therefore prone to impact of floodwaters (possibly storm surge in other locations if located at the beach) and may require extra armoring in these contexts. | The strength of the armouring and strengthening is also dependent on the quality of the concrete (e.g. rebar, water quality, concrete mix) and installation. As it's not pre-fabricated it's dependent on the skills/diligence of the installer. Pre-fabricated concrete modules could achieve armouring and reduce this risk, however, it comes with transport challenges (and also means local masons are not involved in construction). As per 'weak point' comment, extra armoring may be relevant if located adjacent to a waterway or coastal area. | Hardening or stiffening the technology or its components against an expected force. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
Oversizing | Yes | Yes | Yes | No | No | Yes | No | No | FALSE |  | TRUE | The ABR is designed for 20L/capita/day and has a peak design factor of 4. Once installed in a place it is difficult to expand. It has some capacity to cope with 'spikes' in usage. However, prolonged usage or a permanent increase in the number of users will mean it reaches it's capacity. | Increasing the buffer capacity of the first chamber may be an option if there is adequate space. Allowing space for additional buffer chambers to be added to the end may be a consideration in the siting of the ABR | Increasing the tolerance or capacity of the technology or its component so that it can accommodate extreme conditions, projected changes in conditions, or changes in number of users. | 💦 🌧 🌊🌵 | 💦 | 🌧 | 🌊 |  |  | 🌵
Shapes that distribute | Yes | Yes | Yes | No | Yes | Yes | Yes | No | FALSE |  | TRUE | The square shape could be problematic with tidal/wave/flood forces on edges. | For ABRs that are located on the edge of a waterway the shape could ensure there are no edges/protrusions in the waterway that could create increased pressuring during high river flows. | The shape of the technology creates more uniform distribution of stress over its cross-section, thus reducing the risk of failure at weaker points. | 💦 🌧 🌊💨🌵 🌡 | 💦 | 🌧 | 🌊 |  | 💨 | 🌵 | 🌡
Circumvention | Yes | Yes | Yes | No | Yes | No | No | No | FALSE |  | FALSE |  |  | Technology materials or designs that allow wind or water to pass through so that the stress on the technology or component is reduced. | 💦 🌧 🌊💨 | 💦 | 🌧 | 🌊 |  | 💨
Sealing and barriers | Yes | Yes | Yes | Yes | No | No | Yes | Yes | TRUE | Sealed inlet chambers, and manholes. If properly constructed, inlet chambers and manholes will prevent ingress from floodwater/seawater entering the ABR | TRUE | The outlet is not sealed, so backflow is possible when water levels are high | You could install a non-return valve on the outlet to prevent backflow from entering chambers Screens for input could reduce clogging from solid waste or other debris. This may also introduce another failure point and also introduces another level of maintenance moving potential downstream failure (clogging over time) upstream (more shorter term challenges such as blocked screens). | Integrating seals, barriers or other forms of protection into the technology to protect critical components or processes from being disrupted by a hazard. | 💦 🌧 🌊🔥🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 |  |  | 🌡 | ☀️
3.Enabling flexibility | [8 empty] | FALSE |  | FALSE
Adaptability | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | FALSE |  | TRUE | The technology needs a minimum amount of water to ensure it can flow between chambers. Reductions in water supply (e.g. drought) would likely reduce water flow potentially reducing it's functionality. Adaptability in this regard is not integrated into the design. It would require some user intervention. In times of increasing flood or rainfall, there may be additional water inputs into the ABR. If retention times were too fast, this would compromise the level of treatment. Discharge to a soak pit (not detailed in the design) could reduce the impact of backflow from raised receiving water levels and may reduce impact on waterway quality during drought periods when dilution capacity of waterways are reduced. | Effluent could be recirculated through the ABR in times of low water. This would require a pumping system which adds cost and complexity to the design. A shut off valve or similar may be useful in times of flood, sea inundation or high rain if water ingreess into the ABR is an issue. | The technology design can be adapted or upgraded easily to function better under the changing environmental conditions (e.g. increasingly wet or increasingly dry conditions). | 💦 🌧 🌊🔥💨🌵 🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
Modular design | Yes | Yes | No | Yes | Yes | Yes | No | No | FALSE |  | TRUE | Module elements (e.g. additional chambers) to the ABR can not be easily removed or bypassed, however could be added if there was space at either end or possibly piped to additional baffles nearby. However, adding on extra modules is not a common practice. | The concrete structure makes removing modules difficult. Providing pipe fitting or junction boxes at the start or end would ease future modifications, as would allowing additional space for more buffers or a parallel systems in the site selection | Additional modules can be added (plug-in type model) or removed to increase or decrease capacity of the system to accommodate variability in demand and environmental conditions. | 💦 🌧 🔥💨🌵 | 💦 | 🌧 |  | 🔥 | 💨 | 🌵
Platform design | Yes | Yes | Yes | Yes | Yes | No | No | No | FALSE |  | FALSE |  |  | The technology shares components with other similar technologies, which makes it easier to transition between technologies to suit customer demand or prevailing environmental conditions. | 💦 🌧 🌊🔥💨 | 💦 | 🌧 | 🌊 | 🔥 | 💨
Redundancy and dive | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | TRUE | Multiple settlement and ABR chambers. If one chamber fails, the other chamber/s will provide a level of treatment. | FALSE | A failure of one chamber will reduce treatment capability (though not result in total loss of treatment) |  | The technology has redundant components that work in parallel, or that act as back-ups to each other, so that if a component(s) fails, the back-up component can take its place and allow the technology to continue functioning. Diversity entails that the redundant / back-up components can perform the same function, but in a different way. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
Signalling | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | FALSE |  | TRUE | It's difficult to know if there are issues until the technology is already having major issues (e.g. toilets can't be flushed). Difficult to know if effluent is being treated adequately. | Remote flow sensing, or flow analogue gauge of flow rates through inlets, chambers and outlets would indicate if the ABR was failing. | The technology, by the nature of how it functions or by intentional design, has a way of signalling to operators or users when the technology requires modification to prevent failure or to enhance its performance. | 💦 🌧 🌊🔥💨🌵 ☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 |  | ☀️
4. Containing failures | [8 empty] | FALSE |  | FALSE
Frangibility | Yes | No | Yes | Yes | Yes | No | No | No | FALSE |  | FALSE |  |  | Less essential components of the technology are designed to breakaway or fail when exposed to a certain level of pressure to protect more essential components of the technology. | 💦 🌊🔥💨 | 💦 |  | 🌊 | 🔥 | 💨
Fail-operational | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | FALSE |  | TRUE | This depends on the degree of damage. It may provide a limited function if damaged (i.e. minor leakage of waste). However, some repairs may require inputs to be stopped or sludge to be removed to access areas for repair. It's not straightforward to isolate chambers. | Options to bypass chambers for repairs when needed may mean the ABR could continue to function while chambers were repaired. | The technology can still provide its overall function even when components or processes are damaged/compromised and undergoing repair. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
Decentralisation | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | TRUE | Decentralised technology, may be connected to several households. In the event of a failure, only a limited number of households connected to the ABR will be impacted. Compared to a sewered technology where large #'s of households would be impacted. | TRUE | Compared to a septic tank, it is still possible that several households will have disrupted sanitation in the event of a failure. The assessment team noted there may be as many as 40 households connected to some ABRs. | Guidelines on maximum number of households to be connected to an ABR. | Failures in decentralised systems (small-scale individual or clustered systems) are isolated locally which prevents failures from cascading and causing outages to many users/households. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
Limiting consequences of complete failure | [8 empty] | FALSE |  | FALSE
Safe disposal | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | TRUE | Materials are concrete, PVC and steel. If destroyed in fire, flood, etc it does not cause environmental pollution beyond the wastewater waste. There are not materials that would leach into groundwater or create other adverse public health affects. | FALSE |  |  | The materials from the destroyed technology are not toxic to the environment or public health and can be safely disposed. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
Reusable materials | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | FALSE |  | TRUE | The broken concrete is generally not easily used for other purposes. | If the chambers were built out of bricks, they could potentially be recovered and used for other purposes. | The materials from the destroyed technology can be reused for other purposes (including rebuilding the technology). | 💦 🌧 🌊🔥💨🌵 🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
Fail-silence | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | TRUE | Waste is held in the tank until it dries out if the ST stops operating which does not pose a continual health risk | TRUE |  | Could consider HDPE linings around the outside of the ABR to limit public health risks in the event of leakage/damage. | If the technology fails so that it cannot be used anymore, no failure will pose a continual health risk to the public or the environment beyond making the technology unavailable for use. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
Facilitating fast recovery | [8 empty] | FALSE |  | FALSE
Repair speed | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | TRUE | Locally available materials Simple construction. If the ABR is physically damaged, it is likely that repairs could be done by local labour using local materials. | FALSE |  |  | The technology, its components, processes, or its operations can be quickly replaced, rebuilt or restored if destroyed or disrupted so that performance downtime or degradation is minimised. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
Accessibility for rapid flaw detection and repair | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | TRUE | Access hatch for repairs. The chambers can be easily accessed for repairs from the ground. | TRUE | Access to some chambers may be difficult if full of sludge or water. This will also present a health risk to those doing repairs. There is also no way to shut off continued use during repairs. | Introduce shut off valve and ways to shut off toilets that feed into the ABR as needed. As noted earlier, the ability to bypass certain chamers would also help in repairing one chamber while others continue to function. A 'repair' procedure and required tools/equipment should be provided with each ABR, and ideally ABRs should only be installed where trained personnel are available to conduct repairs safely. | Components or processes of the technology can be easily accessed for examination. | 💦 🌧 🌊🔥💨🌵 🌡☀️ | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
Providing benefits beyond resilience | [8 empty] | FALSE |  | FALSE
Reciprocity | No | No | No | No | No | No | No | No | FALSE |  | TRUE |  | If a soak pit or leach field was incorporated into the design, it could incorporate plantings to provide other functionality (e.g. animal feed), assuming it could be done without public health risk. | By providing its service, the technology produces outputs that build resilience in, or aid, another on-site or off-site system.
Hybridising | No | No | No | No | No | No | No | No | TRUE | Surface can be used as a road/hard surface | FALSE |  |  | Unrelated systems or technologies share the same physical space or structure, thus saving space and enhancing opportunities for reciprocity.
Transformative capacity | No | No | No | No | No | No | No | No | FALSE |  | FALSE |  |  | The technology provides an additional service(s) beyond its usual intent that further aids resilient communities.

## Hazard_Calc (hidden)
Code | Hazards | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️ | Relevant | Count |  | Score | Low Impact | Moderate Impact | High Impact | Comments | String | 💦 | 🌧 | 🌊 | 🔥 | 💨 | 🌵 | 🌡 | ☀️
A1 | Landslides (forces, burying) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ⛔️ No | 1 | 0 | - | FALSE | FALSE | FALSE |  | 💦 | 💦
A3 | Corrosion | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | ✅ Yes | 2 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | The ABR is deployed in an area of high groundwater and is/will be subject, flooding, high rainfall and coastal inundation. The concrete construction (armouring and strengthening) likely provides some mitigation to buoyancy forces. However, because it is buried and the nature of the hazard/CIDs there is still potential for moderate impact. | 🌊🌵 |  |  | 🌊 |  |  | 🌵
A4 | Erosion | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | ✅ Yes | 2 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | Salt water from coastal flooding could corrode the rebar in the ABR, weakening it over time. Corrosion will be difficult to observe as rebar is not exposed. | 💦🌊 | 💦 |  | 🌊
A5 | Expansion / contraction of soils (forces on buried structures) | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | ✅ Yes | 4 | Low Impact | Low Impact | TRUE | FALSE | FALSE | The nature of this hazard depends on the reactivity of the soils. If the ABR is installed to specifications (with appropriate concrete mixes, i.e armoring and strengthening), this is unlikely to be an issue. | 🌧🌊🌵🌡 |  | 🌧 | 🌊 |  |  | 🌵 | 🌡
A6 | Exposure to flames | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | ✅ Yes | 1 | Low Impact | Low Impact | TRUE | FALSE | FALSE | The concrete construction (armoring and strengthening) means impact of flames would be minimal on the main ABR structure. Most of the pipes going to the ABR are buried. Those that are exposed are at risk of melting/failure. However the pipes are accessibile for rapid flaw detection and repair, and would be able to be repaired quickly in the case of a fire assuming parts were available. | 🔥 |  |  |  | 🔥
A7 | Force of flood waters | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | ✅ Yes | 2 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | The concrete construction (armoring and strengthening) and burying of the ABR, mean force of flood waters will have minimal impact when located away from rivers or coastal areas. If inlet pipes are not secured or buried, they may present a risk of failure. If the system is partially exposed to flood water, such as on the river bank or coastline, flood waters are more of a concern. | 💦🌊 | 💦 |  | 🌊
A8 | Increased inflow velocity | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | ✅ Yes | 2 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | If the pressure head for the treatment is high and/or inflow velocity is hight, the residence time in various chambers will be reduced, reducing treatment effectiveness. | 💦🌊 | 💦 |  | 🌊
A9 | Increased inflow volume | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | ✅ Yes | 2 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | If the pressure head for the treatment is high and/or inflow velocity is hight, the residence time in various chambers will be reduced, reducing treatment effectiveness. | 💦🌊 | 💦 |  | 🌊
A10 | Increased levels of receiving waterways | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ✅ Yes | 1 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | Backflow or restricted discharge due to raised receiving water levels could reduce residence time and function of the ABR = low impact. Extended periods and flat terrain could cause backflow to the toilet = medium impact. Overall in Banjarmasin this is medium impact as it is quite likely and very flat. | 💦 | 💦
A12 | Reduced inflow velocity | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | ✅ Yes | 1 | Low Impact | Low Impact | TRUE | FALSE | FALSE | A regular flow of water drives flows through the ABR. Reduced velocity is ok, it will increase the pathogen treatment time in each chamber. | 🌵 | [5 empty] | 🌵
A13 | Reduced inflow volume | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | ✅ Yes | 1 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | Reduced water inflow volumes may mean an increase in pathogen concentration in the chambers (less diultion). It's likely the ABR can buffer and reductions in flow volume and increase in pathogen concentration through a longer treatment time because of the reduced flows. Water is required to move waste from toilets to ABR to be treated, so as long as water volume is not below these required levels, impacts will be lower. | 🌵 | [5 empty] | 🌵
A14 | Rise in groundwater level and/or groundwater saturation | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | ✅ Yes | 3 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | The ABR is deployed in an area of high groundwater and is/will be subject, flooding, high rainfall and coastal inundation. The concrete construction (armouring and strengthening) likely provides some mitigation to buoyancy forces. However, because it is buried and the nature of the hazard/CIDs there is still potential for moderate impact. | 💦🌧🌊 | 💦 | 🌧 | 🌊
A16 | Temperature driven expansion/contraction of materials (forces on infrastructure) | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | ⛔️ No | 3 | 0 | - | FALSE | FALSE | FALSE |  | 🔥🌡☀️ |  |  |  | 🔥 |  |  | 🌡 | ☀️
A17 | Uprooting of trees (impact on buried structures) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | ✅ Yes | 1 | Low Impact | Low Impact | TRUE | FALSE | FALSE | It's unlikely uprooted trees would impact the ABR as an excavated site is necessary for its installation. This would only be an issue if trees grew over time and roots were adjacent/under components | 💨 |  |  |  |  | 💨
A18 | Variable inflow velocity | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | ✅ Yes | 1 | Low Impact | Low Impact | TRUE | FALSE | FALSE | Variable inflow velocity (low and high) can be accommodated by the ABR to a point. Refer to comments above on high flows. | 🌧 |  | 🌧
A19 | Variable inflow volume | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | ✅ Yes | 1 | Low Impact | Low Impact | TRUE | FALSE | FALSE | Variable inflow volume (low and high) can be accommodated by the ABR to a potint. Refer to comments above on high flows. | 🌧 |  | 🌧
A20 | Water ingress / inundation | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | ✅ Yes | 2 | High Impact | High Impact | FALSE | FALSE | TRUE | If the pressure head for the treatment is high and/or inflow velocity is high, the residence time in various chambers will be reduced, reducing treatment effectiveness. | 💦🌊 | 💦 |  | 🌊
A21 | Wind force on sanitation structures | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | ✅ Yes | 1 | Low Impact | Low Impact | TRUE | FALSE | FALSE | The ABR is buried and heavy, wind is unlikely to impact the structure. | 💨 |  |  |  |  | 💨
A22 | Wind-blown debris (e.g. trees) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | ✅ Yes | 1 | Low Impact | Low Impact | TRUE | FALSE | FALSE | The technology is buried underground so that windblown debris damage is less likely. Depending on location of pipes, they could be struck by debris or debris clogging inlet, but this is lower risk | 💨 |  |  |  |  | 💨
B1 | Biological organisms exposed to saltwater | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | ✅ Yes | 1 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | Would have less BOD removal and less pathogen removal, but the ABR would still function in terms of physical flow | 🌊 |  |  | 🌊
B2 | Changes in pathogen concentration in inflow | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | ✅ Yes | 2 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | The ABR would be able to reduce pathogens, but if the concentration became very high or if there were a cholera outbreak, the effluent may be poor quality | 💦🌵 | 💦 |  |  |  |  | 🌵
B3 | Changes to biological processes or biota (e.g. algal blooms or pond drying impacting biological treatment) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ✅ Yes | 2 | Low Impact | Low Impact | TRUE | FALSE | FALSE | Extreme heat would have little affect on the structure and treatment processes which are insulated underground | 🌡☀️ | [6 empty] | 🌡 | ☀️
B9 | Rapid change in inflow temperature | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ⛔️ No | 2 | 0 | - | FALSE | FALSE | FALSE |  | 🌡☀️ | [6 empty] | 🌡 | ☀️
B10 | Reduced dilution capacity of receiving waters | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | ✅ Yes | 1 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | Given the system discharges to the waterway and no soak pit (from the scoping tab) the discuarge of this effluent to stressed waterways may become forbidden. Heat stress causing low river flow also increases impact of effluent compared with high flow periods | 🌵 | [5 empty] | 🌵
C1 | Disrupted access to ST for O&M | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | ✅ Yes | 4 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | If maintenance is needed, such as removing a blockage, the technology would fail without the maintenance people being able to access the technology. As sludge removal is irregular, this is unlikely to be an issue except in a severe incident where emergency maintenance was needed. | 💦🌊🔥💨 | 💦 |  | 🌊 | 🔥 | 💨
C2 | Disrupted access to ST for major repairs | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | ✅ Yes | 4 | High Impact | High Impact | FALSE | FALSE | TRUE | If a blockage causes the ABR to be unable to receive new waste, the technology would not be able to be used at all until it can be access for maintenance | 💦🌊🔥💨 | 💦 |  | 🌊 | 🔥 | 💨
C3 | Disrupted electricity inputs to ST | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | ✅ Yes | 5 | Low Impact | Low Impact | TRUE | FALSE | FALSE | The technology does not rely on electricity. It is assumed that sewage is fed into the ABR via gravity. | 💦🌊🔥💨☀️ | 💦 |  | 🌊 | 🔥 | 💨 |  |  | ☀️
C4 | Disrupted FS/excreta collection and delivery | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | ✅ Yes | 4 | Moderate Impact | Moderate Impact | FALSE | TRUE | FALSE | Depending how badly the ABR needs desludging, performance could be degraded to different levels | 💦🌊🔥💨 | 💦 |  | 🌊 | 🔥 | 💨
C5 | Disrupted water inputs to ST | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | ✅ Yes | 5 | High Impact | High Impact | FALSE | FALSE | TRUE | Faecal waste cannot be moved from the toilet to the ABR without water | 💦🌊🔥💨🌵 | 💦 |  | 🌊 | 🔥 | 💨 | 🌵
💦
🌧
🌊
🔥
💨
🌵
🌡
☀️
⁉